## Slide 2
City of East Moline
November 4, 2024
Water System Master Plan - Summary Presentation

## Slide 3
Presentation Outline
Condition of Existing Facilities
Major Findings
Prioritized Capital Improvement Plan
  CIP projects driven by condition, age, and regulatory requirements.

## Slide 4
  Raw Water Pumping Station
  Water Treatment Plant
  21st Avenue Pumping Station
  Elevated Storage Tanks
  Distribution System
Existing Water System

## Slide 5
Condition evaluated based on visual assessment, age, and maintenance history.
  RWPS is in fair condition with some equipment in poor condition.
    Needs new electrical gear and replacement of the PAC system.
  WTP is in fair to good condition and is expected to last another 15 to 20 years with ongoing maintenance.
  Chemical system modifications would bring areas into compliance with current codes.
Condition Assessments

## Slide 6
Condition Assessments
RWPS and WTP require improvements to prolong equipment life.

## Slide 7
Population projections show flat growth
Average Day Demand ~4.4 MGD
Maximum Day Demand ~6.5 MGD
Treatment and pumping capacities sufficient for existing and future demands
Historical and Projected Water Demands

## Slide 8
Overall risk scores for vertical assets and distribution system confirmed condition assessments
Based on the probability of failure and consequences of failure for assets
Asset Management

## Slide 9
Compared East Moline water department Full Time Equivalent staffing to industry standards
17.5 FTE employees
Compared to AWWA standards data suggests additional staff may be warranted
    USEPA’s Lead and Copper Rule Revisions and Improvements
    PFAS regulations
  Add up to six FTE employees to stay in range
Operations Review

## Slide 10
Currently replacing ~0.3% of the system each year.
  Would take 333 years to replace all pipes (some pipes would be >300 years old before replacement)
Risk-based approach recommended by AWWA used to estimate replacement needs.
Increasing replacement to 4% per year for seven years to address critical areas. Annual cost of $10 to $12 million.
Annual Water Main Replacements

## Slide 11
Critical Needs Over Next 10 Years
Major Needs over Next 10 Years | Projected 10-yr Cost in Water Master Plan | Projected Alternative 10-yr Cost
LSL Replacement Mandate | $22,932,000 | $22,932,000
Clearwell Replacement | $15,000,000 | $15,000,000
WTP Maintenance, Replacements, Repairs | $13,780,000 | $13,780,000
Administration and Garage Facility | $13,000,000 | $0
Water Main Replacement Program | $95,000,000 | $54,000,000
Total | $159,712,000 | $105,712,000